HYDRO GENERATOR

Excitation System Testing

Testing Procedures, Specifications & Quality Assurance Standards

Applicable Standards: IS:4722  •  IEC:60034  •  IEEE:115  •  ANSI C34.2

# 1. Introduction

A series of tests are performed on hydroelectric synchronous generators to ensure the following objectives:

- Quality control of components.

- Factory assembly and testing at the manufacturer's facility for quality assurance and to confirm that assemblies meet the required specifications.

- Field assembly and tests for quality control checks of field assemblies.

- Performance tests to ensure that units meet contractual performance guarantees.

- To provide a benchmark of the as-built condition, serving as an aid in future maintenance and repair activities.

Type tests are performed on one unit of a serial purchase (e.g., tests for ensuring conformity with contractual guarantees). Routine tests are performed on every generator in a multi-unit plant.

# 2. Quality Assurance Plan at Manufacturing Works

The quality assurance plan provides details of inspections, tests, and customer witness/hold points for each major component of each functional assembly. The tests include material composition and properties, Non-Destructive Testing (NDT) such as X-ray, hydraulic tests, leakage tests, insulation tests, high voltage tests, and functional tests, along with applicable standards and acceptance criteria. The approved quality plan forms the basis for the inspection and acceptance of equipment.

# 3. Test Specification

The generator specifications should contain a comprehensive and clearly phrased section covering factory and field tests. All required tests should be explicitly listed, with specific test values identified where they differ from IS standards. Specific test procedures, if required or preferred, should be identified.

# 4. Type Tests and Routine Tests

## 4.1 Type Tests

The following constitute the type tests:

- Measurement of winding resistance.

- Phase sequence test.

- Regulation test.

- Measurement of leakage reactances and Potier reactance.

- Measurement of open-circuit characteristic.

- Measurement of short-circuit characteristic.

- Efficiency test.

- Temperature-rise test.

- Over-speed test.

- Insulation resistance test (both before and after dielectric test).

- Dielectric test.

- Determination of deviation of voltage waveform from sinusoidal.

## 4.2 Routine Tests

The following constitute the routine tests:

- Measurement of winding resistance.

- Insulation resistance test.

- Phase sequence test.

- Regulation test.

- Measurement of open-circuit characteristic.

# 5. Testing of Generators up to 5 MW Unit Size

These are usually Category 1 or Category 2 generators, as defined below.

- Category 1: Factory-assembled generators supplied to site completely assembled. These are generally up to 1 MW unit size.

- Category 2: Factory-assembled generators supplied at site as two integral component parts — rotor and stator. These are generally between 0.5 MW and 5 MW unit size.

These categories of generators should meet test requirements as per IS: 4722.

## 5.1 Factory Assembly Test

Factory assembly tests shall include, but are not limited to, the following:

- Dynamic balancing of rotor at 125% rated speed.

- Efficiency test.

- Non-Destructive Testing (NDT) of rotor shaft and shaft coupling bolts.

- Material test certificates of various component parts.

- Temperature rise test.

## 5.2 Field Acceptance Test

Field acceptance tests (all units) consist of:

- Stator dielectric tests: insulation resistance and polarization index. Test voltage for dielectric tests shall be as per IS: 4722.

- Rotor dielectric tests.

- Stator and rotor resistance tests.

## 5.3 Performance Test

Special field tests (one unit of series) consist of:

- Efficiency tests.

- Heat run tests.

- Machine parameter tests.

- Excitation test.

- Over-speed tests.

Note: Full over-speed test should be performed for all units up to 3 MW.

# 6. Testing of Generators Above 5 MW Unit Size

These generators may be Category 2 (refer to Section 5) or one of the following categories:

- Category 3: Generators that require field assembly of the stator, but whose rotor can be shipped to site as an integral component part. These are usually up to 25 MW.

- Category 4: Generators that require complete assembly of the stator and rotor at the site.

## 6.1 Field Acceptance Tests on Generators Above 5 MW

Field acceptance tests shall include the following:

- Phase sequence check.

- Mechanical balance — a field check of mechanical balance of all machines should be carried out.

- Measurement of insulation resistance of stator and rotor winding, including polarization index test.

- Measurement of bearing insulation resistance.

- Open-circuit saturation curves.

- Short-circuit saturation curves.

## 6.2 Performance Tests on Generators Above 5 MW

- Current balance.

- No-load / open-circuit saturation curves.

- Short-circuit saturation curves (synchronous impedance curves).

Note: For generators with brushless exciters, readings of exciter rotor current may be taken in place of generator rotor current.

- Over-speed.

- Impedance of rotor coils.

- Temperature rise tests.

- Harmonic analysis and measurement of Telephone Harmonic Factor (THF).

- Short-circuit withstand tests and measurements of reactances and time constants.

- Efficiency tests by measurement of segregated losses.

- Bearing current (shaft voltage).

# 7. Test Procedures

## 7.1 Dielectric Tests of Stator and Rotor Winding

### 7.1.1 Test Voltages

Standard test voltages of power frequency (as near as possible to a sine wave) for generators as per IS: 4722 are as follows. This test ensures that the insulation is capable of enduring temporary over-voltages.

- Stator winding of generators: 1,000 Volts + twice the rated voltage.

- Overall machines, after cleaning and drying, are subjected to a test voltage of 1.5 times the rated voltage.

### 7.1.2 Stator Winding Turn Insulation Test

The turn insulation of multi-turn coils may be tested as per IEEE Std. 522, by special agreement.

## 7.2 Insulation Resistance Tests and Other Diagnostic Tests

DC voltage insulation resistance tests shall be carried out as per the procedure given in IS: 7816. The polarization index test is an important diagnostic technique and provides trend data for the electrical insulation system.

Other available techniques for this purpose are as follows:

- Power factor and power factor tip-up tests (IEEE Std. 286).

- DC high voltage tests (IEEE Std. 95).

- Various partial discharge (Corona tests) — IEEE Std. 1434.

- Partial discharge tests performed on individual coils and bars, or on complete windings.

The acceptable value depends upon the type of insulation. Ionization probe tests are useful for assessing the condition of individual coils.

## 7.3 Testing High Voltage Terminal Bushings

High voltage terminal bushings (when used) may be tested independently of the machine winding. They should withstand 1.5 times the 1-minute AC test voltage of the machine winding (IEEE Std. C50-12).

## 7.4 Over-Speed Test

As per Clause 17 of IS: 4722.

## 7.5 Short-Circuit Withstand Test

As per Clauses 19 and 20 of IS: 4722.

## 7.6 Vibration

As per IS: 12075.

## 7.7 Noise Test

As per ISO: 3746.

# 8. Excitation System Testing

## 8.1 Static Excitation System — Factory Tests

Factory tests shall be carried out as per the relevant IS standard or IEEE Std. C57.12.91-2001. Routine tests should include measurement of the following:

- Continuity of rectifier fuses.

- Polarity and phase relationships.

- Range and stability of rectifier phase control.

- High potential test in accordance with IEEE Std. 421.3-1997.

## 8.2 Type Tests — Excitation System

Certified test reports are required if a type test is performed. Type tests shall include:

- Rated current and watt losses.

- Temperature rise (heat run).

- Burn-in test: 48 hours, unless otherwise specified.

- Verification of current balance between parallel bridges.

## 8.3 Brushless Excitation System — Factory Tests

- Insulation resistance.

- Resistance of all windings at a specified temperature.

- Resistance of all external current-limiting resistors and field rheostats, where applicable.

# 9. Testing of Large Generators

Any generator that must be assembled in the powerhouse will require field testing after installation to measure efficiency values and reactances, particularly when efficiency guarantees are included in the purchase specification. Normally this requires a second generator in the powerhouse with special switching equipment and a back-fed excitation system to permit retardation tests for determining generator efficiency. Special arrangements are also required to use one of the generator voltage-class breakers as a shorting breaker during sudden short-circuit tests.

Calibration of test instruments and shipping of necessary switchgear and excitation equipment requires considerable lead time. If the associated turbine is to be given a field efficiency test, it may be desirable to coordinate the turbine and generator tests so that the electrical testing instruments are available to measure generator output during the turbine test.

The heat run requires a load on the generator. Normally, the generator is loaded by connecting its output to the system load. If system load is not sufficient, IEEE 115 outlines alternative techniques to simulate load conditions.

Generator erectors usually apply dielectric tests on the armature (stator) and field windings before the rotor is placed into the machine. If the stator is wound in the field, a high potential test is typically performed once each day on all coils installed during that day. The test voltages for intermediate tests must be planned so that each successive test has a lower value than the previous, but greater than the final high potential test voltage.

IS: 7816 describes the polarization index test. This index is the ratio of the insulation resistance obtained with a 10-minute application of test voltage to that obtained with a 1-minute application. Recommended indices and insulation resistance values are given in the referenced standard.

Fire Protection Systems: Generators with closed air recirculation systems are provided with automatic carbon dioxide extinguishing systems. On larger open-ventilated generators, water spray installations are typically provided.

## 9.1 Large Generator Factory Tests

Factory tests for large generators shall include the following:

- Polarization index values for both armature and field windings.

- Stator core loop test at rated flux for one hour.

- Phase rotation check.

- No-load saturation test.

- Short-circuit saturation test.

- Mechanical balance of rotor.

- Dynamic balancing of rotor at 125% rated speed.

- Current transformer test.

- Efficiency test.

- Non-Destructive Testing (NDT) of rotor shaft and shaft coupling bolts.

- Material test certificates of various component parts.

- Temperature rise test.

- Hydrostatic test of each oil/air cooler.

- Power factor tip-up of stator coil insulation.

Note: Air coolers shall be subjected to a static water pressure of 5.25 kg/cm² for a period of not less than one hour without showing leaks.

## 9.2 Excitation System — Routine Factory Tests

Each excitation system should be subjected to routine tests, including but not restricted to the following:

- Dielectric tests per IEC/IS/ANSI C34.2 “Practices and Requirements for Power Rectifiers”.

- Complete operational check of sequencing and regulator sections, set to simulate actual operating conditions.

- Complete operational check of all protective relays.

- Energize all power circuits for operational checks.

- Rated voltage test.

- Test of excitation system potential transformer in accordance with IS:11171 / IEC:35415 / ANSI C57.12.00.

## 9.3 Excitation System — Special Factory Tests

Tests on the excitation system shall be conducted in accordance with ANSI C34.2. The Contractor shall notify the Purchaser in advance when each excitation system will be ready for test, so that the tests may be witnessed by the Purchaser's Inspector.

The Contractor shall furnish certified copies of the factory test report, including characteristic curves. The test report shall include descriptions of the tests performed, sample calculations, and the formulas used.

The following curves and data shall be included in the test report:

- Efficiency and power factor plotted against amperes output through a fixed resistance equal to the calculated resistance of the generator field winding at 75°C.

- Segregated and total losses, plotted against amperes output through a fixed resistance equal to the calculated resistance of the generator field winding at 75°C.

- Excitation system voltage response plotted against percent excitation system error signal.

- Computation of excitation system ripple voltage.

All other electrical parts, such as manual voltage adjusters and similar devices, shall be tested individually in accordance with applicable ANSI, IEEE, or IEC Standards. The Contractor shall submit certified test data covering each part.

# 10. Field Tests

After the generator and auxiliary equipment has been installed in the power plant and is ready for operation, each generator shall be tested by the erection supervisor in the presence of the Engineer in Charge to determine whether the manufacturer's guarantees and the requirements of the specifications have been fulfilled.

The tests shall be conducted in accordance with the latest applicable requirements of IEC Standards, British Standards, ASA Standards, NEMA, and:

- IEEE-115: Test Code for Synchronous Machines (June 1995).

- ASME Test Code for Hydraulic Prime Movers (May 1999) or the latest revision.

Field winding dielectric test: the field windings shall be given a dielectric test for one minute when connected to the interpoles through field leads and the generator collector rings, with all other windings grounded.

## 10.1 Field Acceptance Tests

Field acceptance tests include the following:

- Resistance test of armature and field winding.

- Operation test and adjustment of the entire excitation system to demonstrate compliance with all operating requirements of the specifications, with special regard to sensitivity and response.

- Test for the determination of the time for brakes to stop the machine safely from rated speed to zero, with the turbine gates fully closed and with exciter field open.

- Phase sequence test.

# 11. Performance Tests

In addition to the above field tests, the following special tests shall be made on one generator:

## 11.1 Conventional Efficiency Test

This test shall include the determination of:

- Exciting circuit losses.

- Fixed losses.

- Direct load losses.

- Stray load losses.

The exciting circuit losses shall be included as part of the generator losses in the determination of overall efficiency by the summation of losses method, as laid down in British Standard No. 269 / IEC Standard.

## 11.2 Temperature Rise Test

Test to determine the maximum temperature rises of the various parts of the generator when operating continuously at maximum rated output, with the water supply to the surface air coolers regulated so that the temperature of the air leaving the cooler is approximately 40°C. Load will be provided by the Purchaser. Cooler capacity shall also be tested.

## 11.3 Machine Parameters Tests

Machine parameters shall be determined in accordance with applicable standards.

## 11.4 Three-Phase Short-Circuit Test

This test shall demonstrate that the generator is capable of withstanding short-circuit stresses without injury when the machine is operating under load. The test shall be made by abruptly short-circuiting the generator when operating at no load, rated frequency, and rated voltage, for a period of not more than 10 seconds. One of the current waves, when recorded on an oscillograph, should be completely offset.

## 11.5 Synchronization

The generator shall be synchronized with the available system for best performance.

## 11.6 Tolerances

Tolerance limits for efficiency, total losses, and power factor shall be in accordance with the International Electrotechnical Commission (IEC) Standards for Electrical Machinery, latest edition.

# 12. Maintenance Tests of Hydro Generator Stator Insulation

## 12.1 Introduction

Stator insulation deterioration due to electrical stresses is not uniform. Coils subjected to a voltage of 5 kV and above (line-end coils) suffer a greater degree of deterioration than the rest, leading to insulation failure and causing large expenses in repair and loss of generating capacity.

Evaluation of in-service stator insulation of large hydro generators during commercial use is required to restrict forced outages and study the general trend of insulation deterioration, and to identify coils in an advanced state of deterioration so that a decision for rewinding or replacement of individual coils can be made.

## 12.2 Causes of Insulation Damage

The causes of failure of stator insulation can be attributed to:

- Partial discharges that occur inside voids in the insulation left during manufacture, leading to erosion in soft materials, microscopic cracks in brittle parts, and formation of chemicals corroding the organic insulation.

- Surface discharges that occur when the semiconducting paint of the insulating portion in the slot, or the anti-corona varnish on the overhang portion of the coil, becomes electrically disconnected from the core iron.

- Weak strand insulation leading to breakdown of main insulation.

- Defective turn-to-turn insulation on multi-turn coils.

- Magnetic particles which, once lodged on the insulation surface, bore into the insulation by the action of the alternating flux, leading to corona discharge and ultimate failure of the ground wall insulation.

The high voltage tests are aimed at confirming that the insulation has sufficient dielectric strength to withstand over-voltages expected during operation. Non-destructive tests are those in which the applied test voltage does not exceed the rated line-to-line voltage.

## 12.3 Classification of Insulation Maintenance Tests

### Non-Destructive Tests — Insulation Resistance

- 60-second insulation resistance test.

- Two-volt test.

- Dielectric absorption test.

- Polarization index test.

- Measurement of partial discharge.

- Slot-discharge test.

- Dissipation factor and dissipation factor tip-up.

- Ionization probe measurement.

- Sonic probe.

### High Voltage Tests — Ground Wall Insulation

- AC power frequency test.

- DC high voltage test.

- DC step voltage test.

- AC 0.1 Hz half sine wave HV test.

- AC power frequency resonance HV test.

### High Voltage Tests — Turn-to-Turn Insulation

- Surge comparison test.

- Surge induction test.

# 13. References and Applicable Standards

| Standard | Description |
| --- | --- |
| IS: 4722-2001 | Rotating electrical machines — Specification |
| IS: 7816-1975 | Guide for testing insulation resistance of rotating machines |
| IS: 11171-1983 | Specification for dry type power transformers |
| IS: 12075-1987 | Mechanical vibration of rotating electrical machines |
| IS: 12802 | Temperature rise measurement of rotating electrical machines |
| IEC: 60034 | Rotating electrical machines |
| IEEE: 115 | Test procedure for synchronous machines |
| IEEE: C50-12-2005 | Standard for salient pole 50 Hz synchronous generators/motors for hydraulic applications rated 5 MVA and above |
| IEEE Std. 1 | General principles for temperature limits in the rating of electrical equipment |
| IEEE Std. 4 | Standard techniques for high voltage testing |
| IEEE Std. 43 | Recommended practice for testing insulation resistance of rotating machinery |
| IEEE Std. 95 | Recommended practice for insulation testing of AC electric machinery (2300 V and above) with high direct voltage |
| IEEE Std. 115 | Test procedures for synchronous machines: Part I — Acceptance and performance testing; Part II — Parameter determination for dynamic analysis |
| IEEE Std. 275 | Thermal evaluation of insulation systems for AC electric machinery employing form-wound pre-insulated stator coils rated 6,900 V and below |
| IEEE Std. 421.3-1997 | High potential test of excitation systems |
| IEEE Std. 286 | Power factor and power factor tip-up tests |
| IEEE Std. 522 | Guide for testing turn insulation of form-wound stator coils for AC rotating machines |
| IEEE Std. 1434 | Partial discharge (Corona) tests |
| ANSI C34.2 | Practices and requirements for semiconductor power rectifiers |
| ANSI C57.12.00 | Distribution, power, and regulating transformers |
| ISO: 3746 | Acoustics — Determination of sound power levels of noise sources |